## Sheet1
Optional Load Calculation
Factor | Quantity | VA Ungrounded | VA Neutral
General lighting load (3va per sq ft) | 0 | 0 | 0
Small Appliance @1500va each | 0 | 0 | 0
Laundry Circuit @1500va | 0 | 0 | 0
Total General lighting load |  | 0 | 0
Neutral load: First 3000 at 100% |  |  | 3000
Neutral load:Next at 35% |  |  | -1050
Net computed Neutral load |  |  | 1950
Appliances (Nameplate Rating)
Range (or cooktop) |  |  | 0
Oven |  |  | 0
Dryer (Nameplate or 5000VA whichever is greater) |  |  | 0
Well pump (240v)
Water heater (240v)
(240v)
Dishwasher |  |  | 0
Garbage Disposer |  |  | 0
Microwave |  |  | 0
Freezer |  |  | 0
Exhaust fans |  |  | 0
Hydro massage tub |  |  | 0
(120v) |  |  | 0
(120v) |  |  | 0
Total Load |  | 0
First 10,000VA at 100% |  | 10000
Balance at 40% |  | -4000
Subtotal |  | 6000 | 1950
Other Loads (add largest only) | LOAD in VA
A/C or heat pump compressors @ 100% |  | 0
Electric Furnace or Thermal storage @ 100% |  | 0
Heat pumps with backup heat strips @ 65% |  | 0
Heating Units (3 or less @ 65%) |  | 0
Heating units (4 or more @ 40%) |  | 0
| Total Volt-Amp | 6000 | 1950
| VA/volts = Amps | 25 | 5.6875
The Division of Building Safety provides the information contained in this calculation sheet for your convenience only. The figures used in this form are an estimate and provided only to illustrate how to complete the form. Actual figures are likely to vary. Please ensure the information provided using this form is accurate and complete. The Division of Building Safety may not be held liable for any incorrect information submitted with this form.